## Slide 1: Understanding and Designing Dedicated Outdoor Air Systems (DOAS)
Stanley A. Mumma, Ph.D., P.E. Prof. Emeritus, Architectural Engineering
Penn State University, Univ. Park, PA
sam11@psu.edu
Web: http://doas-radiant.psu.edu
Short Course

## Slide 2: Presentation Outline
Quick review of current leading building HVAC system issues
Define DOAS
Explain terminal equipment choices and issues
Describe DOAS equipment choices and psychrometrics
Provide a DOAS design example
30% surplus OA, why and does it use more energy?
Explain relevance of DOE and ASHRAE Research findings
Describe field applications
Conclusions

## Slide 3: Key Presentation Points
Problems with common VAV systems
DOAS defined
DOAS Issues
Parallel sensible terminal equipment choices
Total Energy Recovery issues and control
Part 1:

## Slide 4: Key Presentation Points
Impact of building pressurization on DOAS
Impact of 30% surplus OA on DOAS
Estimating OA load—it’s not the coil load
DOE Report: DOAS ranks first
System Selection Matrix
Conclusions
Part 2:

## Slide 5: Current HVAC System of Choice: VAV
Std. VAV AHU
VAV
OA
Space 1,
VAV w/ single air delivery path

## Slide 6: Inherent Problems with VAV Systems
Poor air distribution
Poor humidity control
Poor acoustical properties
Poor use of plenum and mechanical shaft space
Serious control problems, particularly with tracking return fan systems
Poor energy transport medium: air
Poor resistance to the threat of biological and chemical terrorism
Poor and unpredictable ventilation performance

## Slide 7
OAreq’d=900 cfm
based on table 6-1
Z1=900/1,500
Z1=0.6
OAreq’d=1,350 cfm
Z2=0.3
AHU
6,000 cfm
% OAB=?
OAB=3,600 cfm
1,500 cfm
4,500 cfm
Over vent=?
1,350 cfm, Unvit
Unvit ratio = 0.225 1,350/6,000
OA=?
OA+(6,000-OA)*0.225=3,600 OA=2,903, ~30% more, but no LEED point 2,903-(900+1,350)=653 more than table 6-1 value Where does the 653 cfm go?
OA=2,250? (900+1,350) No!
OA=3,600? No! Why not?
60
Eq. for OA?
Poor & Unpredictable Vent’n Performance

## Slide 8: Can VAV Limitations Be Overcome?
OAreq’d=900 cfm
Z1=1
OAreq’d=1,350 cfm
Z2=1
AHU
2,250 cfm
% OAB =100
900 cfm
1,350 cfm
OA=2,250
Condition of supply air, DBT & DPT?
How is the space load handled, when 6,000 cfm required for a VAV?
DOAS ?

## Slide 9: DOAS Defined for This Presentation
20%-70% less OA, than VAV
DOAS Unit w/ Energy Recovery
Cool/Dry Supply
Parallel Sensible Cooling System
High Induction Diffuser
Building with Sensible and Latent Cooling Decoupled
Pressurization

## Slide 10: Key DOAS Points
100% OA delivered to each zone via its own ductwork
Flow rate generally as spec. by Std. 62.1 or greater (LEED, Latent. Ctl)
Employ TER, per Std. 90.1
Generally CV
Use to decouple space S/L loads—Dry
Rarely supply at a neutral temperature
Use HID, particularly where parallel system does not use air

## Slide 11: DOAS Issues: ALL ARE IMPORTANT
Reserve capacity
EW issues, including control
SA Conditions
30% surplus OA for a LEED point
Lost air side economizer
Filtration/Terror resistance
Pressurization/floor component 62.1/unbalanced flow @ EW
Toilet Exh/recirc. Air
Direct/indirect evap. Cool
Terminal equipment—series vs. parallel

## Slide 12: Total Energy Recovery (TER) Wheel

## Slide 13: High Induction Diffuser
Provides complete air mixing
Evens temperature gradients in the space
Eliminates short-circuiting between supply & return
Increases ventilation effectiveness

## Slide 14: Parallel Terminal Systems
Fan Coil Units
Air Handling Units CV or VAV
Unitary ACs i.e., WSHPs
Radiant Cooling Panels
Chilled Beams
DOAS air
Induction Nozzle
Sen Cooling Coil
Room air
VRV Multi-Splits
Notes: When talking about integration of dedicated outdoor air systems with parallel terminal systems, as this symposium is based, I wanted to make it clear that we mean anything from
fan coil units,
small air handlers,
unit ventilators in schools,
or just unitary air conditioners.
But the focus of this presentation will be dedicated to radiant cooling panels.

## Slide 16: DOAS employing Parallel VAV
Std. VAV AHU
OA Economizer
OA
Outdoor air unit with TER
Space 2,
DOAS in
parallel w/
VAV
VAV

## Slide 17: VAV Problems Solved with DOAS/Parallel VAV
Poor air distribution
Poor humidity control
Poor acoustical properties
Poor use of plenum and mechanical shaft space
Serious control problems, particularly with tracking return fan systems
Poor energy transport medium: air
Poor resistance to the threat of biological and chemical terrorism
Poor and unpredictable ventilation performance

## Slide 18: DOAS employing Parallel FCU
Outdoor air unit with TER
OA
FCU
Space 3,
DOAS in parallel w/
FCU
Other ways to introduce OA at FCU? Implications?

## Slide 19: Parallel vs. Series OA Introduced for DOAS-FCU Applications?
Parallel, Good Series, Bad

## Slide 20: Advantages of the Correct Paradigm Parallel FCU-DOAS Arrangement
At low sensible cooling load conditions, the terminal equipment may be shut off—saving fan energy
The terminal device fans may be down sized since they are not handling any of the ventilation air, reducing first-cost
The smaller terminal fans result in fan energy savings
The cooling coils in the terminal FCU’s are not derated since they are handling only warm return air, resulting in smaller coils and further reducing first-cost
Opportunity for plenum condensation is reduced since the ventilation air is not introduced into the plenum near the terminal equipment, for better IAQ

## Slide 21: VAV Problems Solved with DOAS/Parallel FCU
Poor air distribution
Poor humidity control
Poor acoustical properties
Poor use of plenum and mechanical shaft space
Serious control problems, particularly with tracking return fan systems
Poor energy transport medium: air
Poor resistance to the threat of biological and chemical terrorism
Poor and unpredictable ventilation performance

## Slide 22: DOAS employing Parallel Radiant, or Chilled Beam
Outdoor air unit with TER
OA
Space 3,
DOAS in parallel w/
CRCP
Radiant Panel

## Slide 23: VAV Problems Solved with DOAS/Radiant-Chilled Beam
Poor air distribution
Poor humidity control
Poor acoustical properties
Poor use of plenum and mechanical shaft space
Serious control problems, particularly with tracking return fan systems
Poor energy transport medium: air
Poor resistance to the threat of biological and chemical terrorism
Poor and unpredictable ventilation performance

## Slide 24: Additional Benefits of DOAS/Radiant-Chilled Beam
Beside solving problems that have gone unsolved for nearly 40 years with conventional VAV systems, note the following benefits:
Greater than 50% reduction in mechanical system operating cost compared to VAV
Equal or lower first cost
Simpler controls
Generates LEED certification points

## Slide 25: DOA Equipment on the Market Today
I: Equipment that adds sensible energy recovery or hot gas for central reheat
II: Equipment that uses total energy recovery
III: Equipment that uses total energy recovery and passive dehumidification wheels
IV: Equipment that uses active dehumidification wheels, generally without energy recovery

## Slide 26: DOAS Equipment on the Market Today K.I.S.S. (II): H/C coils with TER
OA
TER
RA
1
2
3
4
PH
CC
5
Space
Fan
SA DBT, DPT to decouple space loads?
Pressurization
FCU

## Slide 27
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
OA
EW
RA
1
2
3
4
5
PH
CC
Space
2
3
4
5
Hot & humid OA condition

## Slide 28: DOAS unit & Energy Recovery
ASHRAE Standard 90.1 and ASHRAE’s new Standard for the Design Of High Performance Green Buildings (189.1) both require most DOAS systems to utilize exhaust air energy recovery equipment with at least 50% or 60% energy recovery effectiveness:
  that means a change in the enthalpy of the outdoor air supply equal to 50% or 60% of the difference between the outdoor air and return air enthalpies at design conditions.
Std 62.1 allows its use with class 1-3 air.

## Slide 29
Climate Zone 60% TER Req’d Std. 189.1-2009 Design Air flow when >80% OA 1A, 2A, 3A, 4A, 5A, 6A, 7, 8 (Moist E. US + Alaska) > 0 cfm (all sizes require TER) 6B > 1,500 cfm 1B, 2B, 5C > 4,000 cfm 3B, 3C, 4B, 4C, 5B > 5,000 cfm

## Slide 30
Chart: Impact of EW on conditioning OA
room | 64.93
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40

## Slide 31
Chart: EW Control regions, KC data 8760 hrs.
| 46.03 | 65 | 70 | 75 | 80 | 85 | 90
+5% RH error | 110.13 | 85.31 | 78.33 | 71.53 | 64.88 | 58.44 | 52.22
Dry > 75F | 49.3 | 48.9 | 48.8 | 47.99 | 47.8 | 47.5 | 46.89 | 46.69 | 45.75 | 45.02 | 44.89 | 44.68 | 44.06 | 43.95 | 43.9 | 43.75 | 43.48 | 43.44 | 43.21 | 43.19 | 43.11 | 42.78 | 42.55 | 42.49 | 41.84 | 41.57 | 41.4 | 40.93 | 40.9 | 37.78 | 37.68 | 36.95 | 36.85 | 36.39 | 35.94 | 35.43 | 35.31 | 34.25 | 33.85 | 33.77 | 32.56 | 30.66 | 29.96 | 26.81 | 26.37 | 26.09 | 25.67 | 25.07 | 24.81 | 24.42 | 22.53 | 22.04 | 21.29 | 20.38 | 19.67
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
Hot humid OA, 2,666 hrs. EW on either method, no difference
EW should be off! 1,255 hrs. If EW on, cooling use increases by 10,500 Ton Hrs (TH).
EW should be off! 1,261 hrs. If EW on, cooling use increases 18,690 TH
EW speed to modulate to hold 48F SAT. 3,523 hrs. If EW full on, cooling use increases by 45,755 TH
EW off. 55 hrs. If on, cooling use increases 115 TH.

## Slide 32
Chart: EW Control regions, KC data 8760 hrs.
| 46.03 | 65 | 70 | 75 | 80 | 85 | 90
+5% RH error | 110.13 | 85.31 | 78.33 | 71.53 | 64.88 | 58.44 | 52.22
Dry > 75F | 49.3 | 48.9 | 48.8 | 47.99 | 47.8 | 47.5 | 46.89 | 46.69 | 45.75 | 45.02 | 44.89 | 44.68 | 44.06 | 43.95 | 43.9 | 43.75 | 43.48 | 43.44 | 43.21 | 43.19 | 43.11 | 42.78 | 42.55 | 42.49 | 41.84 | 41.57 | 41.4 | 40.93 | 40.9 | 37.78 | 37.68 | 36.95 | 36.85 | 36.39 | 35.94 | 35.43 | 35.31 | 34.25 | 33.85 | 33.77 | 32.56 | 30.66 | 29.96 | 26.81 | 26.37 | 26.09 | 25.67 | 25.07 | 24.81 | 24.42 | 22.53 | 22.04 | 21.29 | 20.38 | 19.67
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
Conclusion: operating the EW in KC all the time for a 10,000 scfm OA system equipped with a 70% effective (e) EW will consume 75,060 extra TH of cooling per year. At 1 kW/ton and $0.15/kWh—this represents $11,260 of waste, and takes us far from NZE buildings.

## Slide 33
Chart: EW Control regions, KC data 8760 hrs.
| 46.03 | 65 | 70 | 75 | 80 | 85 | 90
+5% RH error | 110.13 | 85.31 | 78.33 | 71.53 | 64.88 | 58.44 | 52.22
Dry > 75F | 49.3 | 48.9 | 48.8 | 47.99 | 47.8 | 47.5 | 46.89 | 46.69 | 45.75 | 45.02 | 44.89 | 44.68 | 44.06 | 43.95 | 43.9 | 43.75 | 43.48 | 43.44 | 43.21 | 43.19 | 43.11 | 42.78 | 42.55 | 42.49 | 41.84 | 41.57 | 41.4 | 40.93 | 40.9 | 37.78 | 37.68 | 36.95 | 36.85 | 36.39 | 35.94 | 35.43 | 35.31 | 34.25 | 33.85 | 33.77 | 32.56 | 30.66 | 29.96 | 26.81 | 26.37 | 26.09 | 25.67 | 25.07 | 24.81 | 24.42 | 22.53 | 22.04 | 21.29 | 20.38 | 19.67
Triangle | 50.47 | 53.53 | 53.47 | 55.94 | 55.73 | 55.68 | 55.62 | 55.62 | 55.62 | 55.62 | 55.45 | 55.05 | 53.84 | 56.09 | 53.74 | 51.91 | 50.01 | 55.69 | 57.64 | 59.64 | 59.52 | 53.71 | 50.91 | 59.61 | 54.69 | 60.85 | 60.39 | 60.21 | 57.13 | 56.78 | 56.72 | 55.91 | 55.62 | 55.28 | 55.28 | 52.95 | 51.83 | 51.29 | 51.03 | 58.09 | 52.86 | 52.09 | 54.39 | 61.78 | 60.2 | 59.91 | 59.36 | 58.93 | 58.2 | 57.49 | 55.05 | 51.68 | 55.72 | 56.96 | 58.01 | 52.6 | 50.49 | 53.11
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
EW should be on! 1,048 hrs. If EW off, cooling use increases by 9,540 Ton Hrs (TH).
EW should be off! 72 hrs. If EW on, cooling use increases 1 TH
EW should be off. 55 hrs. If EW on, cooling use increases 115 TH.

## Slide 34
Chart: EW Control regions, KC data 8760 hrs.
| 46.03 | 65 | 70 | 75 | 80 | 85 | 90
+5% RH error | 110.13 | 85.31 | 78.33 | 71.53 | 64.88 | 58.44 | 52.22
Dry > 75F | 49.3 | 48.9 | 48.8 | 47.99 | 47.8 | 47.5 | 46.89 | 46.69 | 45.75 | 45.02 | 44.89 | 44.68 | 44.06 | 43.95 | 43.9 | 43.75 | 43.48 | 43.44 | 43.21 | 43.19 | 43.11 | 42.78 | 42.55 | 42.49 | 41.84 | 41.57 | 41.4 | 40.93 | 40.9 | 37.78 | 37.68 | 36.95 | 36.85 | 36.39 | 35.94 | 35.43 | 35.31 | 34.25 | 33.85 | 33.77 | 32.56 | 30.66 | 29.96 | 26.81 | 26.37 | 26.09 | 25.67 | 25.07 | 24.81 | 24.42 | 22.53 | 22.04 | 21.29 | 20.38 | 19.67
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
+5% error in RH reading. Causes EW to be off when it should be on. 206 hours, 270 extra TH of cooling needed, costing $40.45 when cooling uses 1 kW/ton and energy costs $0.15/kWh
-5% error in RH reading. Causes EW to be on when it should be off. 34 hours, 25 extra TH of cooling needed, costing $3.80 when cooling uses 1 kW/ton and energy costs 0.15/kWh

## Slide 35
Chart: EW Control regions, KC data 8760 hrs.
| 46.03 | 65 | 70 | 75 | 80 | 85 | 90
+5% RH error | 110.13 | 85.31 | 78.33 | 71.53 | 64.88 | 58.44 | 52.22
Dry > 75F | 49.3 | 48.9 | 48.8 | 47.99 | 47.8 | 47.5 | 46.89 | 46.69 | 45.75 | 45.02 | 44.89 | 44.68 | 44.06 | 43.95 | 43.9 | 43.75 | 43.48 | 43.44 | 43.21 | 43.19 | 43.11 | 42.78 | 42.55 | 42.49 | 41.84 | 41.57 | 41.4 | 40.93 | 40.9 | 37.78 | 37.68 | 36.95 | 36.85 | 36.39 | 35.94 | 35.43 | 35.31 | 34.25 | 33.85 | 33.77 | 32.56 | 30.66 | 29.96 | 26.81 | 26.37 | 26.09 | 25.67 | 25.07 | 24.81 | 24.42 | 22.53 | 22.04 | 21.29 | 20.38 | 19.67
Triangle | 50.47 | 53.53 | 53.47 | 55.94 | 55.73 | 55.68 | 55.62 | 55.62 | 55.62 | 55.62 | 55.45 | 55.05 | 53.84 | 56.09 | 53.74 | 51.91 | 50.01 | 55.69 | 57.64 | 59.64 | 59.52 | 53.71 | 50.91 | 59.61 | 54.69 | 60.85 | 60.39 | 60.21 | 57.13 | 56.78 | 56.72 | 55.91 | 55.62 | 55.28 | 55.28 | 52.95 | 51.83 | 51.29 | 51.03 | 58.09 | 52.86 | 52.09 | 54.39 | 61.78 | 60.2 | 59.91 | 59.36 | 58.93 | 58.2 | 57.49 | 55.05 | 51.68 | 55.72 | 56.96 | 58.01 | 52.6 | 50.49 | 53.11
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
If a DBT error of 1F caused the EW to operate above 76F rather than 75F, that 1F band contains 153 hours of data. It would increase the cooling load by 2,255 TH and increase the operating cost by $338 assuming 1 kW/ton cooling performance and $0.15/kWh utility cost. It would also make it impossible to down-size the cooling plant/equip!!!!

## Slide 36
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40

## Slide 37
6
1
2
3
4
5
7
DOAS Equipment on the Market Today

## Slide 38
Chart: Dry Bulb Temperature, F
| 0 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
db=40 | 36.45 | 0
db=60 | 77.48 | 0
db=80 | 156.12 | 0
db=100 | 160 | 0
db=120 | 160 | 0
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
Hot & humid OA condition
1
2
4
6
3
5

## Slide 39: DOAS Equipment on the Market Today
Type 3
Desiccant added for 3 reasons: 1. 45°F CHWS still works 2. achieve DPT < freezing 3. reduce or eliminate reheat

## Slide 40
Chart: Dry Bulb Temperature, F
| 0 | 25 | 40 | 60 | 90 | 120
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
w=80 | 80 | 80
w=120 | 120 | 120
w=160 | 160 | 160
room | 64.89
room h | 84.5 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
2
1
4
5
6
7
3
2
1
4
5
6
7
3
Enthalpy 4 > 3
DOAS needs

## Slide 41: Top DOAS unit Configuration Choices

## Slide 42: A Few Additional Comments Regarding DOAS Equipment
TER Effectiveness is an important factor
TER desiccant an important choice
TER purge, pro and con
Fan energy use management
Reserve capacity must be considered: many benefits
Importance of building pressurization, and the impact on TER effectiveness when unbalanced flow exists
Smaller DOAS with a pressurization unit

## Slide 43: Part 2
Impact of building pressurization on DOAS
Impact of 30% surplus OA on DOAS
Estimating OA load—it’s not the coil load
DOE Report: DOAS ranks first
System Selection Matrix
Conclusions

## Slide 44
Total OA flow per Std. 62.1
Relief air
Toilet & Bldg Exh.
Exfiltration from Pressurization flow
A
B
B
+
= A
Air Flow Paths for a Typical All-Air System

## Slide 45
Relief air,
Toilet & Bldg Exh.
Exfiltration from Pressurization flow
TER
OA
DOAS w/ Unbalanced Flow at the TER

## Slide 46
Relief air,
Toilet & Bldg Exh.
Exfiltration from Pressurization flow
TER
OA
DOAS w/ Balanced Flow at the TER + Pressurization Unit
Pressurization: 4056-1685=2371 cfm ~0.07 cfm/ft2

## Slide 47
Unbalance @ TER if pressurization is ½ ACH, based upon Std. 62.1
Exception to std 90.1 Energy Recovery: Not req’d if exhausted airflow is less than 75% of the required OA. What does that mean in light of pressurization?

## Slide 48
Only 40% of supply is returned to EW, i.e. highly unbalanced flow

## Slide 49
hOA
hSA
mOA
hRA
hEA
mRA
For unbalanced flow, mOA= mRA + mPressurization
e = mOA(hOA-hSA)/mRA(hOA-hRA) = (hEA-hRA)/(hOA-hRA)
eapparent = e*mRA/mOA = (hOA-hSA)/ (hOA-hRA)
Supply air
Wheel Rotation
Return air, including toilet exhaust
Outdoor air
0 scfm Purge or seal leakage
Exhaust air

## Slide 50
Balanced Lecture Conf. rm Educ. Office
Recovered MBH based upon an 85F 140 gr OA condition, an 75F 50% RA condition, and a 130” Dia EW (519 sfpm FV OA stream)

## Slide 52
Integrated DOAS-
Pressurization Units.
Phys & Functionally

## Slide 53
Leadership in Energy and Environmental Design

## Slide 54
IE Q Credit 2: Increased Ventilation: 1 Point
Intent
To provide additional outdoor air ventilation to improve indoor air quality (IAQ) and promote occupant comfort, well-being and productivity.
Requirements
CASE 1. Mechanically Ventilated Spaces
Increase breathing zone outdoor air ventilation rates to occupied spaces by at least 30% above the minimum
rates required by ASHRAE Standard 62.1 (with errata but without addenda1) as determined by IEQ
Prerequisite 1: Minimum Indoor Air Quality Performance.
Sustainable site | 26 | 24%
H2O h | 10 | 9%
Energy & Atmos. | 35 | 32%
Mat’ls & Resource | 14 | 13%
IEQ | 15 | 14%
Innovation | 6 | 5%
Regional Priority | 4 | 4
Max points | 110 | 
Gold: 60-79 points |  | 
Is this a good reason for 30% surplus ventilation air?

## Slide 55: 30% Surplus Air Questioned!

## Slide 56: Calculating the OA load:
75F
50% RH
75F 50% RH
hSA
900 cfm
1,350 cfm
hOA
1: QOA1=mOA*(hOA-hSA)
2: QOA2=mOA*(hOA -hrelief)
QBldg=mSA*(hrelief-hSA)=QOA1-QOA2
So, QOA2 is correct: QOA1=QOAcorrect+QBldg= coil load
hRelief
mOA
mSA= mOA
AHU
Very important to get correct!

## Slide 57
ASHRAE HQ, Atlanta, GA
ASHRAE uses 30%
surplus OA.
And at least one
notable past
president thought
it was a bad idea!

## Slide 58: Limits of LEED authority
Is it rational to increase the ventilation air flow rate beyond 62.1? Many think not.
Can LEED be ignored? Yes
To date there is no mandate in LEED, or the law, to garner this point, and many may in fact choose to garner a LEED point by the much simpler installation of a bicycle rack.

## Slide 59: Why Question 30% Surplus OA? First Consider a Standard VAV System
Std. VAV AHU
VAV
OA
Space 1,
VAV w/ single air delivery path
CC
HC
Fan
Economizer
IEQ
AHU 1st cost
Chiller 1st cost
Boiler 1st cost
Elec. Serv to bldg 1st cost
Conclusion? Energy/Env
RH Allowed by std 90.1?

## Slide 60: Why Question 30% Surplus OA? Consider DOAS
CC
HC
Fan
Economizer
IEQ
AHU 1st cost
Chiller 1st cost
Boiler 1st cost
Elec. Serv to bldg 1st cost
Conclusion? (1st, op, LCC, env)
OA
EW
RA
1
2
3
4
5
PH
CC
Space

## Slide 61: How does the 62.1 flow impact DOAS design—w/ space latent load decoupled?
 | Occ. Category | cfm/p | SA DPT 0F | 1.3*cfm/p | SA DPT 0F
A | Conf. rm | 6.2 | 24.84 | 8.06 | 34.75
B | Lec. cl | 8.42 | 35.9 | 10.96 | 41.63
C | Elem. cl | 11.71 | 42.75 | 15.23 | 46.08
D | Office | 17 | 47.18 | 22.1 | 49.2
E | Museum | 9 | 31.05 | 11.7 | 38.56
?
Key reason to overventilate!
Elevate SA DPT.

## Slide 62: Required SA DPT vs. cfm/person
40%
16%
8%
4%
 | Occ. Category
A | Conf. rm
B | Lec. cl
C | Elem. cl
D | Office
E | Museum
Increasing the latent load (200 to 250 Btu/hr-p) for a given SA flow rate, requires a lower SA DPT.
Knee of curve around 18 cfm/person
A
A’
B
B’
C
C’
D
D’
E
E’

## Slide 63: S.S. CO2 PPM vs. cfm/person
Knee of curves ~18 cfm/p i.e. increased cfm/p yields minimal returns
Assumes an OA CO2 conc. of 400 PPM & an occupant CO2 gen. rate of 0.31 L/min. Note: CO2 conc. is a measure of dilution, i.e. IEQ

## Slide 64: 30% Surplus Conclusion
These 3 hypotheses confirmed:
  A TER device substantially reduces the summer cooling energy used to treat OA.
  30% surplus air is quite beneficial in the winter at reducing the cooling plant energy use.
  The winter savings offsets the added cooling energy use during the warm months for Atlanta, New Orleans, Columbus OH, and Int’l Falls.

## Slide 65: 30% Surplus Conclusion
Increasing the ventilation air to spaces with low OA cfm/person yields big dividends in terms of allowing the SA DPT to be elevated while still accommodating all of the occupant latent loads.
I.e., if a space combined minimum OA/person is ~ 18 cfm/person, do not increase the OA. But for spaces with the 6 to 18 cfm/person range, increase those values upward close to 18 cfm/person.
Then step back and assess how close the entire building ventilation has approached a total 30% increase.

## Slide 66: 30% Surplus Conclusion
If, after equalizing the flow rate per person to about 18 cfm, the 30% surplus ventilation has been achieved, take the LEED point.
Note, if achieved, the LEED point is simply a by-product of elevating the SA DPT.
Otherwise abandon the goal of gaining a LEED point by this method (time to consider the bike rack?!:)—but don’t reduce the cfm/person!!!!

## Slide 67: 30% Surplus Conclusion
Increasing the OA flow rate beyond 18 cfm/person yields diminishing returns in terms of increasing the required SA DPT or enhanced IEQ achievement.

## Slide 68: DOE Report: Ranking of DOAS and Parallel Radiant Cooling
Energy Consumption Characteristics of Commercial Building HVAC Systems: Volume III, Energy Savings Potential
Available at: http://doas-radiant.psu.edu/DOE_report.pdf

## Slide 69
#1
#2
#3
#3

## Slide 70
Both DOAS and Radiant Have Instant Paybacks

## Slide 71: What Has ASHRAE-Sponsored Research Found?
censored
Office: 1 story 6,600 ft2
Retail: 1 story 79,000 ft2

## Slide 72: Base Case: DX, 350 cfm/ton

## Slide 73: DX (400 cfm/ton) with Desiccant

## Slide 74: DOAS w/ Desiccant + DX
350 cfm/ton
400 cfm/ton

## Slide 75: DOAS w/ EW + DX
CC
CC
350 cfm/ton
400 cfm/ton

## Slide 76: Performance for Office, Based upon 62.1-2004 Ventilation Req’d
Location | Miami | Hous | Shrev | Ft. Wor | Atlant | DC | St. Lo | NY | Chic | Port
DX w/ Desiccant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DOAS w/ Des. +DX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DOAS w/ EW +DX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DX w/ Desiccant | 52% | 23 | 18 | 12 | 9 | 1 | -2 | 1 | -8 | -1
DOAS w/ Des. +DX | 48% | 18 | 14 | 8 | 8 | -3 | -5 | -6 | -14 | -8
DOAS w/ EW +DX | -18% | -21 | -20 | -19 | -19 | -23 | -26 | -19 | -26 | -14
Base DX | 37 | 37 | 36 | 40 | 35 | 40 | 38 | 55 | 40 | 35
DOAS w/ Des. +DX | 54 | 48 | 46 | 48 | 44 | 47 | 45 | 63 | 45 | 42
DOAS w/ EW +DX | 35 | 35 | 33 | 37 | 33 | 37 | 35 | 52 | 37 | 36
Annual Op Cost vs. Base DX
Humidity Control (Occ. Hours >65% RH)
LCC: Equipment 1st + 15 yr Gas and Electric $, 1,000’s 2004 dollars

## Slide 77: Performance for Retail, Based upon 62.1-2004 Ventilation Req’d
Location | Miami | Hous | Shrev | Ft. Wor | Atlant | DC | St. Lo | NY | Chic | Port
DX w/ Desiccant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DOAS w/ Des. +DX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DOAS w/ EW +DX | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DX w/ Desiccant | 169 | 79 | 75 | 47 | 61 | 18 | 14 | 6 | -11 | -2
DOAS w/ Des. +DX | 137 | 53 | 44 | 20 | 20 | -9 | -11 | -14 | -30 | -15
DOAS w/ EW +DX | -39 | -42 | -41 | -42 | -41 | -51 | -54 | -44 | -55 | -28
Base DX | 505 | 544 | 522 | 565 | 484 | 606 | 577 | 784 | 610 | 471
DOAS w/ Des. +DX | 999 | 889 | 820 | 799 | 712 | 753 | 739 | 965 | 710 | 633
DOAS w/ EW +DX | 405 | 404 | 387 | 406 | 387 | 423 | 401 | 595 | 433 | 431
Annual Op Cost vs. Base DX (%)
Humidity Control (Occ. Hours >65% RH)
LCC: Equipment 1st + 15 yr Gas and Electric $, 1,000’s 2004 dollars

## Slide 78: Do Other DOAS-Radiant Systems Currently Exist—in the US?
Let’s look briefly at one

## Slide 79
Municipal Building, Denver
ASHRAE tour site:
Denver summer meeting

## Slide 80
Sys. Alts | IAQ (5) (wtg) | 1st $ (5) | Op. $ (4) | DBT Ctl. (3) | Plenum depth (5) | AHU (1) | Future Flex (4) | Maint (3) | Ductwork (2) | Noise (2) | Total Score
FCU w/ DOAS | 5/25 | 7/35 | 1/4 | 1/3 | 6/30 | 8/8 | 1/4 | 1/3 | 6/12 | 1/2 | 126
VAV, HW RH | 4/20 | 5/25 | 3/12 | 5/15 | 2/12 | 4/4 | 5/20 | 7/21 | 2/4 | 7/14 | 145
LT VAV, HW RH | 4/20 | 6/30 | 4/16 | 6/18 | 3/30 | 4/4 | 6/24 | 7/21 | 3/6 | 7/14 | 183
FPVAV, HW RH | 2/10 | 4/20 | 5/20 | 4/12 | 4/20 | 8/8 | 3/12 | 3/9 | 4/8 | 2/4 | 123
FPVAV, Chw recool | 1/5 | 3/15 | 6/24 | 3/9 | 5/25 | 8/8 | 4/16 | 2/6 | 7/14 | 3/6 | 128
LT DDVAV | 3/15 | 2/10 | 2/8 | 2/6 | 1/5 | 4/4 | 2/8 | 4/12 | 1/2 | 5/10 | 80
UFAD | 6/30 | 1/5 | 7/28 | 8/24 | 8/40 | 4/4 | 8/32 | 5/15 | 8/16 | 4/8 | 202
CRCP-DOAS | 8/40 | 8/40 | 8/32 | 7/21 | 7/35 | 8/8 | 7/28 | 8/24 | 5/10 | 8/16 | 254
Category Feature rating/score
System performance in a category (i.e. 1st cost) rating 1-8 (8 Best): i.e. FCUw/ DOAS meeting 1st cost earns a 7
Importance weighting of a category 1-5 (5 most important)
Score: in a cell: product of importance weighting and system performance. i.e. for CRCP-DOAS in the category of Op $, the score is 4*8=32
Conventional VAV 145 pts: DOAS-Rad 254 pts
Max points, 272: VAV 53%, DOAS-Rad 90%

## Slide 81: A Few Other DOAS Applications

## Slide 82
ASHRAE HQ, Atlanta, GA
DOAS unit

## Slide 83
ASHRAE HDQ DOAS unit
VRV Outdoor Units

## Slide 85
Middle School w/ DOAS

## Slide 86
Air Cooled DX DOAS unit

## Slide 88
Chiller serving 2-pipe FCU’s

## Slide 89
  Two Office Towers, Alexandria, VA 17 Tenant Floors 1,300,000 ft2 tenant space
4 @ 85,000 cfm DOAS Units (~0.22 cfm/ft2)

## Slide 91: Conclusion
DOAS offers the following benefits:
  Assured ventilation performance
  Excellent IEQ
  Low energy use compared to all-air systems
  Much simpler controls compared to VAV
  Competitive first-cost
Congratulations to those of you already designing/building/using DOAS !!!!!!!!

## Slide 92
Questions

## Slide 94: Air Side Economizer Lost: Implications!
This a frequent question, coupled with the realization that without full air side economizer, the chiller may run many more hours in the winter than owners and operators would expect based on their prior experiences.
The following slides will address this issue.
For more details, please check the link: http://doas-radiant.psu.edu/IAQ_Econ_Pt1_Pt2.pdf

## Slide 95: 100% Air Side Economizer Lost!
6.5.1 Air (100% OA) or Water (via a cooling tower) Economizers: a prescriptive requirement
11.1.1 Energy Cost Budget Method, an alternative to the prescriptive provisions. It may be employed for evaluating the compliance of all proposed designs. Requires an energy analysis.

## Slide 96: Air Side VAV Econ. Performance Vs. DOAS
An example, assuming:
Internally dominated cooling load building. Fully occupied 6 days per week, from 6 am to 7 pm (13 hours per day, 4,056 hours per year).
100,000 cfm design supply air flow rate at 55°F
Minimum ventilation air requirement: 20,000 cfm
In the economizer mode, the OA flow can modulate between 20,000 cfm and 100,000 cfm
Therefore, the only variability in chiller energy consumption/demand is the economizer control and the geographic location

## Slide 97: Objective
Show that DOAS w/o economizer uses less energy than VAV with economizer
Assumes:
0.7 kW/ton cooling
Fan eff. 70%: Motor eff. 90%
Electricity: $0.08/kWh
AHU internal DP=3”, External DP=4”

## Slide 98
28
140
168
196
112
84
56
Humidity ratio (grains/lb)
Min OA Region: 2766 hrs, Miami, FL 685 hrs, Columbus, OH. 206 hrs, Int’l Falls, MN.
Min OA Region if Enthalpy Ctl, or 100% OA if DBT Ctl: 691 hrs, Miami, FL 419 hrs, Columbus OH. 193 hrs, Int’l Falls, MN.
100% OA Region: 523 hrs, Miami, FL 1058 hrs, Columbus OH. 886 hrs, Int’l Falls, MN.
Modulating OA Region: 76 hrs, Miami, FL 1894 hrs, Columbus OH. 2771 hrs, Int’l Falls, MN.
OA Design: Miami, 311 T Columbus, 290 T Int’l Falls, 271 T
Load if 100% OA, 560 T by design or malfunction

## Slide 99: Economizers frequently experience malfunctioning problems, including stuck or improperly operating dampers. Malfunctions can be minimized as follows:
Quality components must be selected and properly maintained.
Economizer dampers must be tested twice annually before entering each cooling and heating season. Item 2 is rarely done because of operational priorities and the frequent inaccessibility of the hardware.

## Slide 100: Industry Advice when Economizers Experience Repeated Problems Ref: http://www.uppco.com/business/eba_8.aspx
The electric utilities recommend, in order to place a lid on high demand, “locking the economizer in the minimum outside air position if an economizer repeatedly fails, and it is prohibitively expensive to repair it.
Although the potential benefits of the economizer’s energy savings are lost, it is a certain hedge against it becoming a significant energy/demand waster.”

## Slide 101
28
140
168
196
112
84
56
Humidity ratio (grains/lb)
Min OA Region: Economizer does not reduce the TH’s in this region compared to DOAS.
100% OA Region if DBT Ctl. vs., Min OA if Enthalpy Ctl: (DOAS) 234 vs. 150 kTH, Miami, FL 122 vs. 87 kTH, Columbus OH. 53 vs. 40 kTH, Int’l Falls, MN.
100% OA Region vs. DOAS: 59 vs. 88 kTH, Miami, FL 94 vs. 171 kTH, Columbus 75 vs. 144 kTH, Int’l Falls
Modul’g OA Region vs. DOAS: 0 vs. 10 kTH, Miami, FL 0 vs. 209 kTH, Columbus OH. 0 vs. 266 kTH, Int’l Falls, MN.
h Econ Savings over DOAS: Miami, $2,184 Columbus, $16,000 Int’l Falls, $18,760
Fan Op. Cost VAV fan energy: $41,500 DOAS fan energy: $8,000 DOAS Fan Savings: $33,500, or 2-15 times Econ savings.

## Slide 102: Economizer Summary
Using water economizer with DOAS-hydronic systems is a good idea, and can save mechanical cooling energy.
It is recommended for applications employing water cooled chillers.
However the DOAS-hydronic systems should not need WSFC to comply with the Energy Cost Budget Method of Std. 90.1.
That’s good, because many projects are too small for cooling towers, but are excellent candidates for DOAS-hydronic.

## Slide 104: Maximize DOAS free cooling, w/ proper EW control, when hydronic terminal equipment used.

## Slide 105
DOAS Unit
Parallel sen. unit
Tempering OA without the loss of air side economizer!

## Slide 106
Midnight
Space T (MRT)
SA DBT
OA DBT
Panel Pump (P2) On
EW on/off
Free cooling performance data

## Slide 107: 2. EW wheel frost control to minimize energy use.

## Slide 108
Chart: Edmonton weather
| 0 | 25 | 40 | 60 | 90 | 120
rh25 | 1.4 | 4 | 9 | 19.3 | 52.6 | 130
rh=50 | 2.75 | 9.55 | 18.2 | 38.44 | 76.8 | 160
rh=75 | 4 | 14.34 | 27.3 | 58 | 160
rh=100 | 5.5 | 19.1 | 36.45 | 77.5 | 110.6 | 160
w=40 | 40 | 40
w=80 | 80 | 80
w=120 | 120 | 120
w=160 | 160 | 160
room | 64.89
room h | 84.5 | 0
db=0 | 5.5 | 0
db=20 | 15 | 0
OA
Process line cuts sat curve: cond. & frost
New process line tangent to sat. curve, with PH.
EAH
New process line with EAH
PH
OA
RA
3
4
5
PH
CC
Space
EAH

## Slide 109: Another EW frost prevention control: Reduced wheel speed.
Very negative capacity consequences when heat recovery most needed (at -10F, wheel speed drops to 2 rpm to prevent frosting), capacity reduced by >40%.
Suggest avoiding this approach to frost control.

## Slide 110: 3. Control to minimize the use of terminal reheat.

## Slide 111: Limit terminal reheat energy use
Reheat of minimum OA is permitted by Std. 90.1. Very common in VAV systems.
Two methods used w/ DOAS to limit terminal reheat for time varying occupancy:
  DOAS SA DBT elevated to ~70F. Generally wastes energy and increases first cost for the parallel terminal sensible cooling equip. (not recommended!)
  Best way to achieve limited terminal reheat is DCV. (saves H/C energy, fan energy, TER eff)
    CO2 based
    Occupancy sensors

## Slide 112: 4. Pressurization control.

## Slide 113: Building Pressurization Control
Pressurization vs. infiltration as a concept.
outside
inside
Pressure-positive
Pressure-neutral
Infiltration Air flow direction
envelope

## Slide 114: Building Pressurization Control
Pressurization vs. exfiltration as a concept.
outside
inside
Pressure-positive
Pressure-neutral
Exfiltration Air flow direction
envelope

## Slide 115: Building Pressurization Control
Active Pressurization Control
outside
inside
Pressure: P2=P1+0.03” WG
Controlled variable, DP
Pressure: P1
Air flow direction, 1,000 cfm
envelope

## Slide 116: Building Pressurization Control
Controlled flow pressuration.
outside
inside
Pressure: P2 > P1
Controlled variable: flow, not P2
Pressure: P1
Air flow direction, 1,000 cfm
envelope
What happens to depen- dent variable P2 if wind vel. increase P1, w/ controlled flow? (pressurization flow no more than 1,000 cfm)?

## Slide 117
Unbalanced flow @ TER if pressurization is ½ ACH, based upon Std. 62.1
i.e. means RA = 70% SA: Leads to unbalanced flow at
DOAS unit

## Slide 118: Impact of unbalanced flow on EW
e =(h4-h3)/(h1-h3), for balanced or press’n unbalanced flow
eapp=(h1-h2)/(h1-h3)=e *mRA/mOA Note: e =eapp w/ bal. flow
eapp (apparent effectiveness) accounts for unbalanced flow.
eapp ≠ net effectiveness (net e, AHRI 1060 rating parameter)
net e accounts for leakage between the RA (exh.) and OA
OA, mOA, h1
h4
h2
RA, mRA, h3

## Slide 119
Chart: Return air flow, scfm, OA flow constant 6000 scfm
| 6000 | 5000 | 4000 | 3000 | 2000
eff vs. EA | 72 | 80.4 | 88.9 | 95.9 | 99.3
eff apparent vs RA flow | 72 | 67 | 59.2667 | 47.95 | 33.1
MBH ratio to balanced flow | 99.9 | 93.1463 | 82.3951 | 66.6622 | 46.0171
effectiveness, e
app. effectiveness, eapp
energy recovery, %
Hi
Low
100% 83% 67% 50% 33%

## Slide 121
Discuss flow based pressurization control

## Slide 122: Conclusions,
Fortunately, DOAS controls are simpler than VAV control systems.
Unfortunately, they require a different paradigm—something the industry is just coming up to speed on.
A properly designed and controlled DOAS will reduce:
  Energy use/demand,
  First cost,
  Humidity problems and related IEQ issues
  Ventilation compliance uncertainty.